## Revisions
Revision | Date | Comments | Inputs | Revised by
0 | 14th Feb 2022 | Based on UK5 AI Furnace Model Input Pre-Processing r16 | 75 | M.McL

## C4 Tags
Tag | TagID Description | Description | LogInterval | TagID | Symbol | FactoryAreaName | Time Lag (Hours) | Time lag increment (20 min steps) | Compression | Eng Min | Eng Max | Indirect TagID | Enable | Filter Low Pass | Parameter Low Pass | Filter Outlliers | Filter Spikes | Filter Reversal | Comments
SHE01:'2#T103_30:PT_P501'.F_PV | 6539 Bath Pressure (PV) | Bath Pressure (PV) | 60 | 6539 | mbar | Bath | 2 | 0 | 0.002 | 0 | 1 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'2#T103_30:PID_T211'.F_OP | 10278 Canal Temperature Centre (OP) | Canal Temperature Centre (OP) | 60 | 10278 | % | Bath | 2 | 0 | 1 | 0 | 100 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'2#T103_30:PID_T211'.F_PV | 10279 Canal Temperature Centre (PV) | Canal Temperature Centre (PV) | 60 | 10279 | °C | Bath | 2 | 0 | 0.1 | 700 | 1300 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'2#T103_30:TT_T211'.F_PV | 1950 Canal Temperature RHS (PV) | Canal Temperature RHS (PV) | 60 | 1950 | °C | Bath | 2 | 0 | 0.1 | 700 | 1300 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_12:PT_P007'.F_PV | 6396 Chimney Draught Pressure | Chimney Draught Pressure | 60 | 6396 | mbar | Furnace | 4 | 0 | 1 | 0 | 6 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set to 1.0 as compared to 0.001 at UK5
SHE01:'1#T103_16:QT_Q002'.F_PV | 332 Chimney Particle Concentration | Chimney Particle Concentration | 60 | 332 | mg/Nm³ | Furnace | 4 | 0 | 1 | 0 | 100 |  | 0 | [5 empty] | Input suspect
SHE01:'1#T103_10:TE_T141'.F_PV | 6398 Chimney Temperature - Base | Chimney Temperature - Base | 60 | 6398 | °C | Furnace | 4 | 0 | 1 | 0 | 1000 |  | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set to 1.0 as compared to 0.1 at UK5
SHE01:'1#T103_10:TE_T142'.F_PV | 6392 Chimney Temperature - Main Flue | Chimney Temperature - Main Flue | 60 | 6392 | °C | Furnace | 4 | 0 | 1 | 0 | 1000 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_22:TE_T049'.F_PV | 2909 Closed Bottom Temperature - Downstream Refiner (PV) | Closed Bottom Temperature - Downstream Refiner (PV) | 60 | 2909 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T051'.F_PV | 2922 Closed Bottom Temperature - Downstream Working End (PV) | Closed Bottom Temperature - Downstream Working End (PV) | 60 | 2922 | °C | Furnace | 2 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlation group 13
SHE01:'1#T103_22:TE_T048'.F_PV | 2908 Closed Bottom Temperature - Mid Refiner (PV) | Closed Bottom Temperature - Mid Refiner (PV) | 60 | 2908 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | No valid signal update since 20/11/2019
SHE01:'1#T103_22:TE_T043'.F_PV | 2913 Closed Bottom Temperature - Port 1 (PV) | Closed Bottom Temperature - Port 1 (PV) | 60 | 2913 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Correlation group 10
SHE01:'1#T103_22:TE_T044'.F_PV | 2914 Closed Bottom Temperature - Port 2 (PV) | Closed Bottom Temperature - Port 2 (PV) | 60 | 2914 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | No valid signal update since 06/01/2016
SHE01:'1#T103_22:TE_T045'.F_PV | 2916 Closed Bottom Temperature - Port 4 (PV) | Closed Bottom Temperature - Port 4 (PV) | 60 | 2916 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | No valid signal update since 31/07/2014
SHE01:'1#T103_22:TE_T046'.F_PV | 2918 Closed Bottom Temperature - Port 6 (PV) | Closed Bottom Temperature - Port 6 (PV) | 60 | 2918 | °C | Furnace | 20 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | No valid signal update since 21/12/2015
SHE01:'1#T103_22:TE_T047'.F_PV | 2907 Closed Bottom Temperature - Upstream Refiner (PV) | Closed Bottom Temperature - Upstream Refiner (PV) | 60 | 2907 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | No valid signal update since 07/07/2016
SHE01:'1#T103_22:TE_T050'.F_PV | 2921 Closed Bottom Temperature - Upstream Working End (PV) | Closed Bottom Temperature - Upstream Working End (PV) | 60 | 2921 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T000'.F_PV | 31107 Closed Crown Temperature - 0/Port 1 (PV) | Closed Crown Temperature - 0/Port 1 (PV) | 60 | 31107 | °C | Furnace | 24 | 0 | 1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Compression set too high, set to 0.1 , Not used for monitoring crown temperature
SHE01:'1#T103_22:TE_T010'.F_PV | 2925 Closed Crown Temperature - Downstream Working End (PV) | Closed Crown Temperature - Downstream Working End (PV) | 60 | 2925 | °C | Furnace | 2 | 0 | 1 | 800 | 1200 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_22:TE_T001'.F_PV | 1675 Closed Crown Temperature - Port 1 (PV) | Closed Crown Temperature - Port 1 (PV) | 60 | 1675 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Not used for monitoring crown temperature
SHE01:'1#T103_22:TE_T002'.F_PV | 1676 Closed Crown Temperature - Port 2 (PV) | Closed Crown Temperature - Port 2 (PV) | 60 | 1676 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Not used for monitoring crown temperature
SHE01:'1#T103_22:TE_T003'.F_PV | 1677 Closed Crown Temperature - Port 3 (PV) | Closed Crown Temperature - Port 3 (PV) | 60 | 1677 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 1 | No data. Tag defintion missing from process server
SHE01:'1#T103_22:TE_T004'.F_PV | 1678 Closed Crown Temperature - Port 4 (PV) | Closed Crown Temperature - Port 4 (PV) | 60 | 1678 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | No valid signal update since 27/12/2016
SHE01:'1#T103_22:TE_T005'.F_PV | 1679 Closed Crown Temperature - Port 5 (PV) | Closed Crown Temperature - Port 5 (PV) | 60 | 1679 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Not used for monitoring crown temperature
SHE01:'1#T103_22:TE_T006'.F_PV | 1680 Closed Crown Temperature - Port 6 (PV) | Closed Crown Temperature - Port 6 (PV) | 60 | 1680 | °C | Furnace | 18 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Not used for monitoring crown temperature
SHE01:'1#T103_16:TE_T007'.F_PV | 1681 Closed Crown Temperature - Upstream Refiner (PV) | Closed Crown Temperature - Upstream Refiner (PV) | 60 | 1681 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Signal suspect, as it appears to be too low
SHE01:'1#T103_22:TE_T009'.F_PV | 6386 Closed Crown Temperature - Upstream Working End (PV) | Closed Crown Temperature - Upstream Working End (PV) | 60 | 6386 | °C | Furnace | 2 | 0 | 1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_16:PID_F061'.F_OP | 9379 Combustion Air Flow - MECA (OP) | Combustion Air Flow - MECA (OP) | 60 | 9379 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_16:PID_F061'.F_PV | 6382 Combustion Air Flow - MECA (PV) | Combustion Air Flow - MECA (PV) | 60 | 6382 | m³/h | Furnace | 24 | 0 | 10 | 0 | 25000 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_16:PID_F061'.F_SP | 9380 Combustion Air Flow - MECA (SP) | Combustion Air Flow - MECA (SP) | 60 | 9380 | m³/h | Furnace | 24 | 0 | 0 | 0 | 25000 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_16:PID_F060'.F_OP | 159 Combustion Air Flow - WECA (OP) | Combustion Air Flow - WECA (OP) | 60 | 159 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_16:PID_F060'.F_PV | 6385 Combustion Air Flow - WECA (PV) | Combustion Air Flow - WECA (PV) | 60 | 6385 | m³/h | Furnace | 24 | 0 | 10 | 0 | 600000 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_16:PID_F060'.F_SP | 160 Combustion Air Flow - WECA (SP) | Combustion Air Flow - WECA (SP) | 60 | 160 | m³/h | Furnace | 24 | 0 | 0 | 0 | 600000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 3
SHE01:'2#T940_32:I_F00060'.F_CV | 5534 Combustion Air Flow Low | Combustion Air Flow Low | 60 | 5534 | Unknown | Furnace | 24 | 0 | 0.1 | 0 | 1 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Digital signal, exclude
SHE01:'1#T103_16:TT_T161'.F_PV | 1650 Combustion Air Temperature (PV) | Combustion Air Temperature (PV) | 60 | 1650 | °C | Furnace | 12 | 0 | 1 | 0 | 50 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:FT_F194'.F_PV | 7434 Cooling Water Flow - Furnace LHS | Cooling Water Flow - Furnace LHS | 60 | 7434 | l/min | Furnace | 0 | 0 | 100 | 0 | 10000 |  | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_20:FT_F195'.F_PV | 6310 Cooling Water Flow - Furnace RHS | Cooling Water Flow - Furnace RHS | 60 | 6310 | l/min | Furnace | 0 | 0 | 100 | 0 | 10000 |  | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_20:TT_T191'.F_PV | 8352 Cooling Water Temperature - Furnace LHS | Cooling Water Temperature - Furnace LHS | 60 | 8352 | °C | Furnace | 0 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:TT_T192'.F_PV | 8346 Cooling Water Temperature - Furnace RHS | Cooling Water Temperature - Furnace RHS | 60 | 8346 | °C | Furnace | 0 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:DIFERENCA.F_CV | 15034 Difference between Actual and Budget Gas Consumption | Difference between Actual and Budget Gas Consumption | 60 | 15034 | m³/h | Furnace | 0 | 0 | 1 | -2000 | 2000 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:ANC01_22'.F_PV8 | 1745 Electric Boost Zone 1 - Total Power (PV) | Electric Boost Zone 1 - Total Power (PV) | 60 | 1745 | kW | Furnace | 24 | 0 | 1 | 0 | 5000 |  | 1
SHE01:'#T103_22:I_PHA_KW'.F_PV | 10285 Electric Boost Zone 1 Phase 1 - Power (PV) | Electric Boost Zone 1 Phase 1 - Power (PV) | 60 | 10285 | kW | Furnace |  |  | 1 | 0 |  |  | 0 | [5 empty] | No data
SHE01:'#T103_22:I_PHB_KW'.F_PV | 10286 Electric Boost Zone 1 Phase 2 - Power (PV) | Electric Boost Zone 1 Phase 2 - Power (PV) | 60 | 10286 | kW | Furnace |  |  | 1 | 0 |  |  | 0 | [5 empty] | No data
SHE01:'#T103_22:I_PHC_KW'.F_PV | 10287 Electric Boost Zone 1 Phase 3 - Power (PV) | Electric Boost Zone 1 Phase 3 - Power (PV) | 60 | 10287 | kW | Furnace |  |  | 1 | 0 |  |  | 0 | [5 empty] | No data
SHE03:BATH_EE_GROSS_WIDTH.F_CV | 10097 Exit End Gross Width | Exit End Gross Width | 60 | 10097 | mm | Bath | 0 | 0 | 1 | 0 | 4200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No valid signal update since 27/12/2015
SHE01:'2#T103_30:TT_T213'.F_PV | 7532 Exit End Pyrometer Temperature Centre (PV) | Exit End Pyrometer Temperature Centre (PV) | 60 | 7532 | °C | Bath | 0 | 0 | 1 | 250 | 1100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_14:ST_S001'.F_PV | 221 Feeder 1 Speed | Feeder 1 Speed | 60 | 221 | rpm | Furnace | 24 | 0 | 1 | 0 | 1500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , correlation group 1
SHE01:'1#T103_14:ST_S002'.F_PV | 224 Feeder 2 Speed | Feeder 2 Speed | 60 | 224 | rpm | Furnace | 24 | 0 | 1 | 0 | 1500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , correlation group 1
SHE01:'1#T103_22:TE_T041'.F_PV | 2911 Filling Pocket Closed Bottom Temperature LHS (PV) | Filling Pocket Closed Bottom Temperature LHS (PV) | 60 | 2911 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T042'.F_PV | 2912 Filling Pocket Closed Bottom Temperature RHS (PV) | Filling Pocket Closed Bottom Temperature RHS (PV) | 60 | 2912 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_14:FT_F171'.F_PV | 5288 Front Wall Cooling Air Flow (PV) | Front Wall Cooling Air Flow (PV) | 60 | 5288 | m³/h | Furnace | 0 | 0 | 0.1 | 0 | 25000 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#T103_12:PT_P008'.F_PV | 6484 Front Wall Cooling Air Pressure | Front Wall Cooling Air Pressure | 60 | 6484 | mbar | Furnace | 0 | 0 | 1 | 0 | 25 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T101'.F_PV | 6482 Front Wall Temperature 1 | Front Wall Temperature 1 | 60 | 6482 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T110'.F_PV | 6481 Front Wall Temperature 10 | Front Wall Temperature 10 | 60 | 6481 | °C | Furnace | 24 | 0 | 0.5 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T111'.F_PV | 6480 Front Wall Temperature 11 | Front Wall Temperature 11 | 60 | 6480 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T112'.F_PV | 6479 Front Wall Temperature 12 | Front Wall Temperature 12 | 60 | 6479 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T102'.F_PV | 6477 Front Wall Temperature 2 | Front Wall Temperature 2 | 60 | 6477 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T103'.F_PV | 6476 Front Wall Temperature 3 | Front Wall Temperature 3 | 60 | 6476 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T104'.F_PV | 6475 Front Wall Temperature 4 | Front Wall Temperature 4 | 60 | 6475 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T105'.F_PV | 6474 Front Wall Temperature 5 | Front Wall Temperature 5 | 60 | 6474 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T106'.F_PV | 6473 Front Wall Temperature 6 | Front Wall Temperature 6 | 60 | 6473 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T107'.F_PV | 6472 Front Wall Temperature 7 | Front Wall Temperature 7 | 60 | 6472 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T108'.F_PV | 7482 Front Wall Temperature 8 | Front Wall Temperature 8 | 60 | 7482 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T109'.F_PV | 7481 Front Wall Temperature 9 | Front Wall Temperature 9 | 60 | 7481 | °C | Furnace | 24 | 0 | 1 | 0 | 250 | 200000 | 1 | 1 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
## | 10091 Furnace Load | Furnace Load | 60 | 10091 | t/w | Production | 2 | 0 | 0 | 0 | 6500 |  | 1 | 1 | 0.1 | 0 | 1 | 0
N/A | Furnace Oxyfuel Firing Total Gas Flow | Furnace Oxyfuel Firing Total Gas Flow | 60 | 15079 | m³/h | Furnace | 0 | 0 | 0 | 0 | 0 |  | 0 | 1 | 0.1 | 0 | 0 | 1 | Data from spreadsheet, have data only after 2021-09-01
SHE01:'1#T103_12:PT_P009'.F_PV | 105 Furnace Pressure - Working End (PV) | Furnace Pressure - Working End (PV) | 60 | 105 | mbar | Furnace | 4 | 0 | 0.001 | -0.1 | 0.3 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_14:PID_P006'.F_OP | 9403 Furnace Pressure (OP) | Furnace Pressure (OP) | 60 | 9403 | % | Furnace | 4 | 0 | 1 | 0 | 100 |  | 1 | 1 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_14:PID_P006'.F_PV | 15119 Furnace Pressure (PV) | Furnace Pressure (PV) | 60 | 15119 | mbar | Furnace | 4 | 0 | 0.001 | 0 | 1 |  | 1 | 1 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_14:PID_P006'.F_SP | 9404 Furnace Pressure (SP) | Furnace Pressure (SP) | 60 | 9404 | mbar | Furnace | 4 | 0 | 0 | 0 | 1 |  | 1 | 1 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_14:PID_L001'.F_OP | 9393 Glass Level (OP) | Glass Level (OP) | 60 | 9393 | % | Furnace | 4 | 0 | 0.1 | 0 | 100 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlation group 1
SHE01:'1#T103_14:PID_L001'.F_PV | 321 Glass Level (PV) | Glass Level (PV) | 60 | 321 | mm | Furnace | 4 | 0 | 0.0005 | -80 | 60 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#T103_14:PID_L001'.F_SP | 9394 Glass Level (SP) | Glass Level (SP) | 60 | 9394 | mm | Furnace | 4 | 0 | 0 | -80 | 60 |  | 0 | 1 | 0.1 | 0 | 1 | 0 | Mostly constant
SHE01:'2#T103_40:S601'.F_CV | 7473 Lehr Drive 1 Speed | Lehr Drive 1 Speed | 60 | 7473 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 9
SHE01:'2#T103_40:S602'.F_CV | 7658 Lehr Drive 2 Speed | Lehr Drive 2 Speed | 60 | 7658 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 9
SHE01:'2#T103_40:S603'.F_PV | 7474 Lehr Drive Line Shaft Speed | Lehr Drive Line Shaft Speed | 60 | 7474 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_12:FT_F050'.F_PV | 10516 Main Gas Flow (PV) | Main Gas Flow (PV) | 60 | 10516 | m³/h | Furnace | 12 | 0 | 1 | 0 | 7000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 5
SHE01:'1#T103_12:PID_P004'.F_OP | 9395 Main Gas Pressure (OP) | Main Gas Pressure (OP) | 60 | 9395 | % | Furnace | 12 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 3
SHE01:'1#T103_12:PID_P004'.F_PV | 6463 Main Gas Pressure (PV) | Main Gas Pressure (PV) | 60 | 6463 | mbar | Furnace | 12 | 0 | 1 | 0 | 2 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.001 , insufficient data
SHE01:'1#T103_12:PID_P004'.F_SP | 9396 Main Gas Pressure (SP) | Main Gas Pressure (SP) | 60 | 9396 | mbar | Furnace | 12 | 0 | 0 | 0 | 2 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Mostly constant
SHE01:'1#T103_12:TT_T151'.F_PV | 6662 Main Gas Supply Temperature | Main Gas Supply Temperature | 60 | 6662 | °C | Furnace | 12 | 0 | 1 | -20 | 80 |  | 0 | 1 | 0.1 | 0 | 1 | 1 | Compression set too high, set to 0.1, Correlation group 11
SHE01:'1#T103_22:TE_T043X'.F_PV | 10373 Open Bottom Temperature - FPC (PV) | Open Bottom Temperature - FPC (PV) | 60 | 10373 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Signal invalid
SHE01:'1#T103_22:TE_T044X'.F_PV | 6301 Open Bottom Temperature - Port 2 (PV) | Open Bottom Temperature - Port 2 (PV) | 60 | 6301 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlation group 10
SHE01:'1#T103_22:TE_T045X'.F_PV | 7745 Open Bottom Temperature - Port 4 (PV) | Open Bottom Temperature - Port 4 (PV) | 60 | 7745 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T046X'.F_PV | 8452 Open Bottom Temperature - Port 6 (PV) | Open Bottom Temperature - Port 6 (PV) | 60 | 8452 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T048X'.F_PV | 2900 Open Bottom Temperature - Port 8 (PV) | Open Bottom Temperature - Port 8 (PV) | 60 | 2900 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T047X'.F_PV | 7690 Open Bottom Temperature - U/S Refiner (PV) | Open Bottom Temperature - U/S Refiner (PV) | 60 | 7690 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T049X'.F_PV | 1732 Open Bottom Temperature - Waist | Open Bottom Temperature - Waist | 60 | 1732 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_22:TE_T000X'.F_PV | 2910 Open Crown Temperature - 0/Port 1 (PV) | Open Crown Temperature - 0/Port 1 (PV) | 60 | 2910 | °C | Furnace | 24 | 0 | 1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1
SHE01:'1#T103_22:TE_T008'.F_PV | 7485 Open Crown Temperature - Downstream Refiner (PV) | Open Crown Temperature - Downstream Refiner (PV) | 60 | 7485 | °C | Furnace | 4 | 0 | 0.1 | 1000 | 1650 |  | 1 | 0 | 0.1 | 0 | 1 | 0
SHE01:'1#T103_22:TE_T003'.F_PV | 7548 Open Crown Temperature - Port 3 (PV) | Open Crown Temperature - Port 3 (PV) | 60 | 7548 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_22:TE_T004X'.F_PV | 7522 Open Crown Temperature - Port 4 (PV) | Open Crown Temperature - Port 4 (PV) | 60 | 7522 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Signal invalid
SHE01:'1#T103_12:PID_F151'.F_OP | 9401 Port 1 Gas Flow (OP) | Port 1 Gas Flow (OP) | 60 | 9401 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 7
SHE01:'1#T103_12:PID_F151'.F_PV | 6467 Port 1 Gas Flow (PV) | Port 1 Gas Flow (PV) | 60 | 6467 | m³/h | Furnace | 0 | 0 | 1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 7
SHE01:'1#T103_12:PID_F151'.F_SP | 9402 Port 1 Gas Flow (SP) | Port 1 Gas Flow (SP) | 60 | 9402 | m³/h | Furnace | 0 | 0 | 0 | 0 | 1200 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_12:PID_F152'.F_OP | 9399 Port 2 Gas Flow (OP) | Port 2 Gas Flow (OP) | 60 | 9399 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 3
SHE01:'1#T103_12:PID_F152'.F_PV | 6466 Port 2 Gas Flow (PV) | Port 2 Gas Flow (PV) | 60 | 6466 | m³/h | Furnace | 0 | 0 | 1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 3
SHE01:'1#T103_12:PID_F152'.F_SP | 9400 Port 2 Gas Flow (SP) | Port 2 Gas Flow (SP) | 60 | 9400 | m³/h | Furnace | 0 | 0 | 0 | 0 | 1200 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_14:PID_F153'.F_OP | 9397 Port 3 Gas Flow (OP) | Port 3 Gas Flow (OP) | 60 | 9397 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 5
SHE01:'1#T103_14:PID_F153'.F_PV | 6465 Port 3 Gas Flow (PV) | Port 3 Gas Flow (PV) | 60 | 6465 | m³/h | Furnace | 0 | 0 | 1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 5
SHE01:'1#T103_14:PID_F153'.F_SP | 9398 Port 3 Gas Flow (SP) | Port 3 Gas Flow (SP) | 60 | 9398 | m³/h | Furnace | 0 | 0 | 0 | 0 | 1200 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_14:PID_F154'.F_OP | 9475 Port 4 Gas Flow (OP) | Port 4 Gas Flow (OP) | 60 | 9475 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 8
SHE01:'1#T103_14:PID_F154'.F_PV | 6665 Port 4 Gas Flow (PV) | Port 4 Gas Flow (PV) | 60 | 6665 | m³/h | Furnace | 0 | 0 | 1 | 0 | 700 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 8
SHE01:'1#T103_14:PID_F154'.F_SP | 9476 Port 4 Gas Flow (SP) | Port 4 Gas Flow (SP) | 60 | 9476 | m³/h | Furnace | 0 | 0 | 0 | 0 | 700 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_16:PID_F155'.F_OP | 9579 Port 5 Gas Flow (OP) | Port 5 Gas Flow (OP) | 60 | 9579 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 6
SHE01:'1#T103_16:PID_F155'.F_PV | 8390 Port 5 Gas Flow (PV) | Port 5 Gas Flow (PV) | 60 | 8390 | m³/h | Furnace | 0 | 0 | 1 | 0 | 900 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlation group 6
SHE01:'1#T103_16:PID_F155'.F_SP | 9580 Port 5 Gas Flow (SP) | Port 5 Gas Flow (SP) | 60 | 9580 | m³/h | Furnace | 0 | 0 | 0 | 0 | 900 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#T103_16:PID_F156'.F_OP | 9461 Port 6 Gas Flow (OP) | Port 6 Gas Flow (OP) | 60 | 9461 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_16:PID_F156'.F_PV | 6585 Port 6 Gas Flow (PV) | Port 6 Gas Flow (PV) | 60 | 6585 | m³/h | Furnace | 0 | 0 | 1 | 0 | 700 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_16:PID_F156'.F_SP | 9462 Port 6 Gas Flow (SP) | Port 6 Gas Flow (SP) | 60 | 9462 | m³/h | Furnace | 0 | 0 | 0 | 0 | 700 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 6
SHE01:PIDF180L.F_OP | 15214 Refiner Burner Gas Flow LHS (OP) | Refiner Burner Gas Flow LHS (OP) | 60 | 15214 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 4
SHE01:PIDF180L.F_CV | 15215 Refiner Burner Gas Flow LHS (PV) | Refiner Burner Gas Flow LHS (PV) | 60 | 15215 | m³/h | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 4
SHE01:PIDF180L.F_SP | 15216 Refiner Burner Gas Flow LHS (SP) | Refiner Burner Gas Flow LHS (SP) | 60 | 15216 | m³/h | Furnace | 0 | 0 | 0 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:PIDF180R.F_OP | 15217 Refiner Burner Gas Flow RHS (OP) | Refiner Burner Gas Flow RHS (OP) | 60 | 15217 | % | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 4
SHE01:PIDF180R.F_CV | 15218 Refiner Burner Gas Flow RHS (PV) | Refiner Burner Gas Flow RHS (PV) | 60 | 15218 | m³/h | Furnace | 0 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 4
SHE01:PIDF180R.F_SP | 15219 Refiner Burner Gas Flow RHS (SP) | Refiner Burner Gas Flow RHS (SP) | 60 | 15219 | m³/h | Furnace | 0 | 0 | 0 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 4
SHE01:'1#T103_22:TE_T021'.F_PV | 1355 Regenerator Crown Temperature Port 2 LHS | Regenerator Crown Temperature Port 2 LHS | 60 | 1355 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300021 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_22:TE_T031'.F_PV | 1358 Regenerator Crown Temperature Port 2 RHS | Regenerator Crown Temperature Port 2 RHS | 60 | 1358 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300021 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_22:TE_T022'.F_PV | 1356 Regenerator Crown Temperature Port 4 LHS | Regenerator Crown Temperature Port 4 LHS | 60 | 1356 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300022 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_22:TE_T032'.F_PV | 1359 Regenerator Crown Temperature Port 4 RHS | Regenerator Crown Temperature Port 4 RHS | 60 | 1359 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300022 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_22:TE_T023'.F_PV | 15069 Regenerator Crown Temperature Port 6 LHS | Regenerator Crown Temperature Port 6 LHS | 60 | 15069 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1, Not enough data to combine in set 2
SHE01:'1#T103_22:TE_T033'.F_PV | 15070 Regenerator Crown Temperature Port 6 RHS | Regenerator Crown Temperature Port 6 RHS | 60 | 15070 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1, Not enough data to combine in set 2
SHE01:'1#T103_10:TE_T122'.F_PV | 10502 Regenerator Inner Flue Temperature LHS | Regenerator Inner Flue Temperature LHS | 60 | 10502 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1, Not enough data to combine in set 2
SHE01:'1#T103_10:TE_T132'.F_PV | 10504 Regenerator Inner Flue Temperature RHS | Regenerator Inner Flue Temperature RHS | 60 | 10504 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1, Not enough data to combine in set 2
SHE01:'1#T103_10:TE_T121'.F_PV | 10503 Regenerator Outer Flue Temperature LHS | Regenerator Outer Flue Temperature LHS | 60 | 10503 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300023 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_10:TE_T131'.F_PV | 10505 Regenerator Outer Flue Temperature RHS | Regenerator Outer Flue Temperature RHS | 60 | 10505 | °C | Furnace | 36 | 0 | 1 | 0 | 1650 | 300023 | 1 | 0 | 0.1 | 0 | 0 | 1 | Compression set too high, set to 0.1
SHE01:'1#T103_20:PIDF173L'.F_OP | 353 Sidewall Cooling Fan Speed LHS (OP) | Sidewall Cooling Fan Speed LHS (OP) | 60 | 353 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:PIDF173L'.F_PV | 354 Sidewall Cooling Fan Speed LHS (PV) | Sidewall Cooling Fan Speed LHS (PV) | 60 | 354 | rpm | Furnace |  |  | 1 | 0 |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Always set to zero
SHE01:'1#T103_20:PIDF173L'.F_SP | 355 Sidewall Cooling Fan Speed LHS (SP) | Sidewall Cooling Fan Speed LHS (SP) | 60 | 355 | rpm | Furnace |  |  | 0 | 0 |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Always set to zero
SHE01:'1#T103_20:PIDF173R'.F_OP | 356 Sidewall Cooling Fan Speed RHS (OP) | Sidewall Cooling Fan Speed RHS (OP) | 60 | 356 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:PIDF173R'.F_PV | 357 Sidewall Cooling Fan Speed RHS (PV) | Sidewall Cooling Fan Speed RHS (PV) | 60 | 357 | rpm | Furnace |  |  | 1 | 0 |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Always set to zero
SHE01:'1#T103_20:PIDF173R'.F_SP | 358 Sidewall Cooling Fan Speed RHS (SP) | Sidewall Cooling Fan Speed RHS (SP) | 60 | 358 | rpm | Furnace |  |  | 0 | 0 |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Always set to zero
SHE01:'1#T103_20:TT_T172'.F_PV | 15121 Stirrer Cooling Water Return Temperature LHS | Stirrer Cooling Water Return Temperature LHS | 60 | 15121 | °C | Furnace | 0 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:TT_T173'.F_PV | 15122 Stirrer Cooling Water Return Temperature RHS | Stirrer Cooling Water Return Temperature RHS | 60 | 15122 | °C | Furnace | 0 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1
SHE01:'1#T103_20:TT_T171'.F_PV | 6421 Stirrer Cooling Water Supply Temperature | Stirrer Cooling Water Supply Temperature | 60 | 6421 | °C | Furnace | 0 | 0 | 0.1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_20:PID_S005'.F_OP | 7570 Stirrer Speed (OP) | Stirrer Speed (OP) | 60 | 7570 | % | Furnace | 4 | 0 | 0.1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Mostly constant
SHE01:'1#T103_20:PID_S005'.F_PV | 1653 Stirrer Speed (PV) | Stirrer Speed (PV) | 60 | 1653 | rpm | Furnace | 4 | 0 | 1 | 0 | 12.4 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Mostly constant
SHE01:'1#T103_20:PID_S005'.F_SP | 1654 Stirrer Speed (SP) | Stirrer Speed (SP) | 60 | 1654 | rpm | Furnace | 4 | 0 | 0 | 0 | 12.4 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Mostly constant
SHE01:'2#T103_30:FT_F201'.F_PV | 7560 Total Working End Cooling Air (PV) | Total Working End Cooling Air (PV) | 60 | 7560 | m³/h | Furnace | 3 | 0 | 10 | 0 | 10000 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlation group 12
SHE01:'2#T103_40:G501'.F_CV | 9282 Tweel Height | Tweel Height | 60 | 9282 | mm | Bath | 2 | 0 | 0 | 0 | 650 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:PIDF184L.F_OP | 31119 Upstream Refiner Burner Gas Flow LHS (OP) | Upstream Refiner Burner Gas Flow LHS (OP) | 60 | 31119 | % | Furnace | 8 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 2
SHE01:PIDF184L.F_PV | 31118 Upstream Refiner Burner Gas Flow LHS (PV) | Upstream Refiner Burner Gas Flow LHS (PV) | 60 | 31118 | m³/h | Furnace | 8 | 0 | 1 | 0 | 140 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 2
SHE01:PIDF184L.F_SP | 31120 Upstream Refiner Burner Gas Flow LHS (SP) | Upstream Refiner Burner Gas Flow LHS (SP) | 60 | 31120 | m³/h | Furnace | 8 | 0 | 0 | 0 | 140 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:PIDF184R.F_OP | 31122 Upstream Refiner Burner Gas Flow RHS (OP) | Upstream Refiner Burner Gas Flow RHS (OP) | 60 | 31122 | % | Furnace | 8 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 2
SHE01:PIDF184R.F_PV | 31121 Upstream Refiner Burner Gas Flow RHS (PV) | Upstream Refiner Burner Gas Flow RHS (PV) | 60 | 31121 | m³/h | Furnace | 8 | 0 | 1 | 0 | 140 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 2
SHE01:PIDF184R.F_SP | 31123 Upstream Refiner Burner Gas Flow RHS (SP) | Upstream Refiner Burner Gas Flow RHS (SP) | 60 | 31123 | m³/h | Furnace | 8 | 0 | 0 | 0 | 140 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlation group 2
SHE01:'1#T103_16:TT_T152'.F_PV | 467 Wobbe Gas Temperature | Wobbe Gas Temperature | 60 | 467 | °C | Furnace | 12 | 0 | 0.1 | -20 | 80 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#T103_16:QT_Q001'.F_PV | 11384 Wobbe Index | Wobbe Index | 60 | 11384 | Unknown | Furnace | 12 | 0 | 1 | 1000 | 1500 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Mostly constant
SHE01:'2#T103_30:PIDF201L'.F_OP | 235 Working End Burner Gas Flow LHS (OP) | Working End Burner Gas Flow LHS (OP) | 60 | 235 | % | Furnace | 2 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1, Correlation group 15 (choosen input)
SHE01:'2#T103_30:PIDF201L'.F_PV | 233 Working End Burner Gas Flow LHS (PV) | Working End Burner Gas Flow LHS (PV) | 60 | 233 | m³/h | Furnace | 2 | 0 | 1 | 0 | 125 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 1
SHE01:'2#T103_30:PIDF201L'.F_SP | 234 Working End Burner Gas Flow LHS (SP) | Working End Burner Gas Flow LHS (SP) | 60 | 234 | m³/h | Furnace | 2 | 0 | 0 | 0 | 125 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 1
SHE01:'2#T103_30:PIDF201R'.F_OP | 15032 Working End Burner Gas Flow RHS (OP) | Working End Burner Gas Flow RHS (OP) | 60 | 15032 | % | Furnace | 2 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 15
SHE01:'2#T103_30:PIDF201R'.F_PV | 239 Working End Burner Gas Flow RHS (PV) | Working End Burner Gas Flow RHS (PV) | 60 | 239 | m³/h | Furnace | 2 | 0 | 1 | 0 | 125 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 1
SHE01:'2#T103_30:PIDF201R'.F_SP | 240 Working End Burner Gas Flow RHS (SP) | Working End Burner Gas Flow RHS (SP) | 60 | 240 | m³/h | Furnace | 2 | 0 | 0 | 0 | 125 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Compression set too high, set to 0.1 , Correlation group 1

## UK5 Tags
Tag | TagID Description | Description | LogInterval | TagID | Symbol | FactoryAreaName | Time Lag (Hours) | Time lag increment (20 min steps) | Compression | Eng Min | Eng Max | Indirect TagID | Enable | Filter Low Pass | Parameter Low Pass | Filter Outlliers | Filter Spikes | Filter Reversal | Comments
SHE01:'1#BC1:PT_P501'.F_CV | 6539 Bath Pressure (PV) | Bath Pressure (PV) | 60 | 6539 | mbar | Bath | 2 | 0 | 0.002 | 0 | 1 |  | 1 | 1 | 0.1 | 0 | 1 | 0 | Low pass filter for feeder noise
SHE01:'1#FC5:FT_F199'.F_CV | 11273 Brownedge Water Supply Flow Meas. | Brownedge Water Supply Flow Meas. | 60 | 11273 | l/min | Furnace | 0 | 0 | 1 | 0 | 1100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Signal invalid
## | 10425 Calculated Cullet Ratio | Calculated Cullet Ratio | 60 | 10425 | % | Batch | 24 | 0 | 0.1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:TT_T201.F_PV | 1951 Canal Temp. Control Pyrometer (1) | Canal Temp. Control Pyrometer (1) | 60 | 1951 | °C | Furnace | 2 | 0 | 0.1 | 1000 | 1200 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | U/S, non-controlling cleaner
SHE01:TT_T211.F_PV | 1950 Canal Temp. Control Pyrometer (2) | Canal Temp. Control Pyrometer (2) | 60 | 1950 | °C | Furnace | 2 | 0 | 0.1 | 1000 | 1200 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | D/S, controlling noisier
SHE01:PID_T201.F_OP | 10278 Canal Temp. Control (OP) | Canal Temp. Control (OP) | 60 | 10278 | % | Furnace | 2 | 0 | 0.1 | -100 | 100 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Possible control loop tuning improvement Correlated with 7945 gropup 5
SHE01:PID_T201.F_PV | 10279 U/S Canal T201 | U/S Canal T201 | 60 | 10279 | °C | Furnace | 2 | 0 | 0.1 | 1000 | 1200 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Relatively noisey signal
SHE01:'1#FC5:PT_P005'.F_CV | 6396 Chimney Draught Pressure | Chimney Draught Pressure | 60 | 6396 | mbar | Furnace | 4 | 0 | 1 | 0 | 6 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:'1#FC7:PT_P010'.F_CV | 11282 Chimney Draught Pressure - After Ecomomiser | Chimney Draught Pressure - After Ecomomiser | 60 | 11282 | mbar | Furnace | 4 | 0 | 1 | 0 | 40 |  | 1 | 1 | 0.1 | 0 | 1 | 0 | Check signal resolution
SHE01:'1#F1:TE_T141'.F_CV | 6398 Chimney Temperature - Base | Chimney Temperature - Base | 60 | 6398 | °C | Furnace | 4 | 0 | 1 | 0 | 1000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#F1:TE_T044'.F_CV | 2909 Closed Bottom Temperature - Downstream Refiner (PV) | Closed Bottom Temperature - Downstream Refiner (PV) | 60 | 2909 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2909 group 9
SHE01:'1#F1:TE_T048'.F_CV | 2922 Closed Bottom Temperature - Downstream Working End (PV) | Closed Bottom Temperature - Downstream Working End (PV) | 60 | 2922 | °C | Furnace | 2 | 36 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T042'.F_CV | 2908 Closed Bottom Temperature - Mid Refiner (PV) | Closed Bottom Temperature - Mid Refiner (PV) | 60 | 2908 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2909 group 9
SHE01:'1#F1:TE_T035'.F_CV | 2913 Closed Bottom Temperature - Port 1 (PV) | Closed Bottom Temperature - Port 1 (PV) | 60 | 2913 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T037'.F_CV | 2914 Closed Bottom Temperature - Port 2 (PV) | Closed Bottom Temperature - Port 2 (PV) | 60 | 2914 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2913 group 6
SHE01:'1#F1:TE_T038'.F_CV | 2916 Closed Bottom Temperature - Port 4 (PV) | Closed Bottom Temperature - Port 4 (PV) | 60 | 2916 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2913 group 6
SHE01:'1#F1:TE_T039'.F_CV | 2918 Closed Bottom Temperature - Port 6 (PV) | Closed Bottom Temperature - Port 6 (PV) | 60 | 2918 | °C | Furnace | 20 | 38 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T040'.F_CV | 1672 Closed Bottom Temperature - Port 8 (PV) | Closed Bottom Temperature - Port 8 (PV) | 60 | 1672 | °C | Furnace | 20 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2909 group 9
SHE01:'1#F1:TE_T041'.F_CV | 2907 Closed Bottom Temperature - Upstream Refiner (PV) | Closed Bottom Temperature - Upstream Refiner (PV) | 60 | 2907 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2909 group 9
SHE01:'1#F1:TE_T047'.F_CV | 2921 Closed Bottom Temperature - Upstream Working End (PV) | Closed Bottom Temperature - Upstream Working End (PV) | 60 | 2921 | °C | Furnace | 24 | 18 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:TT_T162.F_PV | 1650 Combustion Air Temperature Measurement | Combustion Air Temperature Measurement | 60 | 1650 | °C | Furnace | 12 | 0 | 0.1 | 0 | 200 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Day to night temperature cycle
SHE01:'1#FC1:M001_581'.F_CV | 30902 Controller FC1 Firing Left | Controller FC1 Firing Left | 60 | 30902 | On/Off | Furnace | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Marks reversal and firing side. Not subtable as an input Meeting 02 Dec 2020
SHE01:'1#FC1:M001_591'.F_CV | 30903 Controller FC1 Firing Right | Controller FC1 Firing Right | 60 | 30903 | On/Off | Furnace | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Not subtable as an input Meeting 02 Dec 2020
SHE01:'1#FC5:FT_F194'.F_CV | 7434 Cooling Water Flow - Furnace LHS | Cooling Water Flow - Furnace LHS | 60 | 7434 | l/min | Furnace | 0 | 0 | 100 | 0 | 15000 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Possible day to night cycle
SHE01:'1#FC5:FT_F195'.F_CV | 6310 Cooling Water Flow - Furnace RHS | Cooling Water Flow - Furnace RHS | 60 | 6310 | l/min | Furnace | 0 | 0 | 100 | 0 | 15000 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Possible day to night cycle
SHE01:'1#FC7:TE_T191'.F_CV | 8352 Cooling Water Temperature - Furnace LHS | Cooling Water Temperature - Furnace LHS | 60 | 8352 | °C | Furnace | 0 | 0 | 1 | 0 | 60 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:'1#FC7:TE_T192'.F_CV | 8346 Cooling Water Temperature - Furnace RHS | Cooling Water Temperature - Furnace RHS | 60 | 8346 | °C | Furnace | 0 | 0 | 1 | 0 | 60 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:'1#F1:TE_T000'.F_CV | 2910 Crown Temp Meas 4m D/S No.8 Port C/L | Crown Temp Meas 4m D/S No.8 Port C/L | 60 | 2910 | °C | Furnace | 12 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 1 | 1 | 1 | Corrrelated with 10271 group 12
SHE01:PID_F201.F_OP | 11149 D/S Working End Cooling Air Flow Control Left (OP) | D/S Working End Cooling Air Flow Control Left (OP) | 60 | 11149 | % | Furnace | 3 | 0 | 0.1 | 0 | 100 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 7945 group 5
SHE01:PID_F201.F_PV | 1727 D/S Working End Cooling Air Flow Control Left (PV) | D/S Working End Cooling Air Flow Control Left (PV) | 60 | 1727 | m³/h | Furnace | 3 | 0 | 10 | 0 | 4500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 7945 group 5
SHE01:PID_F211.F_OP | 11152 D/S Working End Cooling Air Flow Control Right (OP) | D/S Working End Cooling Air Flow Control Right (OP) | 60 | 11152 | % | Furnace | 3 | 0 | 0.1 | 0 | 100 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 7945 group 5
SHE01:PID_F211.F_PV | 1728 D/S Working End Cooling Air Flow Control Right (PV) | D/S Working End Cooling Air Flow Control Right (PV) | 60 | 1728 | m³/h | Furnace | 3 | 0 | 10 | 0 | 4500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 7945 group 5
SHE01:EEDS_AVERAGE_GROSS_WIDTH.F_CV | 5134 EEDS Average Gross Width Measurement | EEDS Average Gross Width Measurement | 60 | 5134 | mm | Bath | 0 | 0 | 1 | 3000 | 4000 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#F2:AN_E015'.F_CV | 11213 Essential Services Board Cat 'B' Supply - MV53 | Essential Services Board Cat 'B' Supply - MV53 | 60 | 11213 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Day to night cycle
SHE01:ST_S001.F_PV | 30208 Feeder Speed Measurement Left | Feeder Speed Measurement Left | 60 | 30208 | rpm | Furnace | 24 | 0 | 0.1 | 0 | 1500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Check signal?
SHE01:ST_S002.F_PV | 30209 Feeder Speed Measurement Right | Feeder Speed Measurement Right | 60 | 30209 | rpm | Furnace | 24 | 0 | 0.1 | 0 | 1500 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Check signal?
SHE01:'1#FPC:TE_T032'.F_CV | 2923 Filling Pocket Closed Bottom Temperature Centre (PV) | Filling Pocket Closed Bottom Temperature Centre (PV) | 60 | 2923 | °C | Furnace | 24 | 11 | 0.1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2913 group 6
SHE01:'1#FPL:TE_T031'.F_CV | 2911 Filling Pocket Closed Bottom Temperature LHS (PV) | Filling Pocket Closed Bottom Temperature LHS (PV) | 60 | 2911 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Possible day to night cycle Ignored from correlated group 7
SHE01:'1#FPR:TE_T033'.F_CV | 2912 Filling Pocket Closed Bottom Temperature RHS (PV) | Filling Pocket Closed Bottom Temperature RHS (PV) | 60 | 2912 | °C | Furnace | 24 | 0 | 0.1 | 0 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Correlated with 2913 group 6
SHE01:'1#FC5:FT_F171'.F_CV | 5288 Front Wall Cooling Air Flow (PV) | Front Wall Cooling Air Flow (PV) | 60 | 5288 | m³/h | Furnace | 0 | 0 | 0.1 | 0 | 40000 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#FC5:PT_P004'.F_CV | 6484 Front Wall Cooling Air Pressure | Front Wall Cooling Air Pressure | 60 | 6484 | mbar | Furnace | 0 | 0 | 1 | 0 | 10 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:'1#F1:TE_T081'.F_CV | 6482 Front Wall Temperature 1 | Front Wall Temperature 1 | 60 | 6482 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T090'.F_CV | 6481 Front Wall Temperature 10 | Front Wall Temperature 10 | 60 | 6481 | °C | Furnace | 24 | 0 | 0.5 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T091'.F_CV | 6480 Front Wall Temperature 11 | Front Wall Temperature 11 | 60 | 6480 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T092'.F_CV | 6479 Front Wall Temperature 12 | Front Wall Temperature 12 | 60 | 6479 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T082'.F_CV | 6477 Front Wall Temperature 2 | Front Wall Temperature 2 | 60 | 6477 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T083'.F_CV | 6476 Front Wall Temperature 3 | Front Wall Temperature 3 | 60 | 6476 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T084'.F_CV | 6475 Front Wall Temperature 4 | Front Wall Temperature 4 | 60 | 6475 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T085'.F_CV | 6474 Front Wall Temperature 5 | Front Wall Temperature 5 | 60 | 6474 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T086'.F_CV | 6473 Front Wall Temperature 6 | Front Wall Temperature 6 | 60 | 6473 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T087'.F_CV | 6472 Front Wall Temperature 7 | Front Wall Temperature 7 | 60 | 6472 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T088'.F_CV | 7482 Front Wall Temperature 8 | Front Wall Temperature 8 | 60 | 7482 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T089'.F_CV | 7481 Front Wall Temperature 9 | Front Wall Temperature 9 | 60 | 7481 | °C | Furnace | 24 | 0 | 1 | 0 | 1000 | 200000 | 0 | 1 | 0.1 | 0 | 0 | 0
To be define | 7532 Exit End Pyrometer Temperature Centre (PV) | Exit End Pyrometer Temperature Centre (PV) | 60 | 7532 | °C | To be define | 0 | 0 | 1 |  |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Temporarily included to investigate a potential correlation with the FFD spikes
SHE01:'1#F2:AN_E003'.F_CV | 11201 Furnace & Services Pack Sub S8 L.H. Section - HV13 | Furnace & Services Pack Sub S8 L.H. Section - HV13 | 60 | 11201 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F2:AN_E006'.F_CV | 11204 Furnace & Services Pack Sub S8 R.H. Section - HV16 | Furnace & Services Pack Sub S8 R.H. Section - HV16 | 60 | 11204 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Day to night cycle Correlated with 11213 group 20
SHE01:TE_T046.F_CV | 11174 Furnace Bottom Temperature 18m D/S of B8 | Furnace Bottom Temperature 18m D/S of B8 | 60 | 11174 | °C | Furnace | 24 | 0 | 1 | 0 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#FC4:FT_F181'.F_CV | 6400 Furnace Compressed Air Flow Measurement | Furnace Compressed Air Flow Measurement | 60 | 6400 | m³/h | Services | 0 | 0 | 10 | 0 | 4000 |  | 0 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#FC2:FT_F150'.F_CV | 31037 Furnace Gas Flow Measurement | Furnace Gas Flow Measurement | 60 | 31037 | m³/h | Furnace | 12 | 0 | 10 | 0 | 8000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Not consider from correlated group 3
## | 10091 Furnace Load | Furnace Load | 60 | 10091 | t/w | Production | 2 | 63 | 0 | 0 | 6500 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#FC6:PID_P006'.F_OP | 9403 Furnace Pressure (OP) | Furnace Pressure (OP) | 60 | 9403 | % | Furnace | 4 | 0 | 1 | 0 | 100 |  | 0 | 1 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC6:PID_P006'.F_PV | 15119 Furnace Pressure (PV) | Furnace Pressure (PV) | 60 | 15119 | mbar | Furnace | 4 | 0 | 0.001 | -1 | 1 |  | 1 | 1 | 0.1 | 0 | 0 | 1
SHE01:PT_P060.F_PV | 6469 Furnace Pressure Meas. on Crown | Furnace Pressure Meas. on Crown | 60 | 6469 | mbar | Furnace | 4 | 0 | 0.001 |  |  |  | 0 | 1 | 0.1 | 0 | 0 | 1
SHE01:PT_P011.F_PV | 105 Furnace Pressure Meas. Working End | Furnace Pressure Meas. Working End | 60 | 105 | mbar | Furnace | 4 | 0 | 0.001 | 0 | 0.5 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Possible signal resolution problem
SHE01:TT_T163.F_PV | 6662 Gas Temperature Measurement | Gas Temperature Measurement | 60 | 6662 | °C | Furnace | 12 | 0 | 0.1 | -10 | 40 |  | 0 | 1 | 0.1 | 0 | 1 | 1 | Temp increases with no flow Correlated with 1650 group 21
SHE01:PID_L001.F_OP | 9393 Glass Level Control (OP) | Glass Level Control (OP) | 60 | 9393 | % | Furnace | 4 | 0 | 0.1 | 0 | 100 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:PID_L001.F_PV | 321 Glass Level Control (PV) | Glass Level Control (PV) | 60 | 321 | mm | Furnace | 4 | 0 | 0.01 | -20 | 20 |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#L1:SI_S601'.F_CV | 7473 Lehr Drive 1 Speed | Lehr Drive 1 Speed | 60 | 7473 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Use line shaft speed
SHE01:'1#L1:SI_S602'.F_CV | 7658 Lehr Drive 2 Speed | Lehr Drive 2 Speed | 60 | 7658 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Use line shaft speed
SHE01:'1#L1:SI_S603'.F_CV | 7474 Lehr Drive Line Shaft Speed | Lehr Drive Line Shaft Speed | 60 | 7474 | m/h | Lehr | 2 | 0 | 0.1 | 0 | 1200 |  | 1 | 0 | 0.1 | 0 | 0 | 0
## | 12720 Line Output (Production) | Line Output (Production) | 60 | 12720 | tonnes | Production | 2 | 0 | 0 |  |  |  | 0 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC5:PID_P003'.F_OP | 9395 Main Gas Pressure (OP) | Main Gas Pressure (OP) | 60 | 9395 | % | Furnace | 12 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Permits to identify relevant inputs that are more meaningful in the control room
SHE01:'1#FC5:PID_P003'.F_PV | 6463 Main Gas Pressure (PV) | Main Gas Pressure (PV) | 60 | 6463 | Bar | Furnace | 12 | 0 | 0.01 | 0 | 2 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F2:AN_E011'.F_CV | 11209 MV49 | MV49 | 60 | 11209 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Day to night cycle
SHE01:'1#F2:AN_E013'.F_CV | 11211 MV51 | MV51 | 60 | 11211 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F1:TE_T009'.F_CV | 7485 MV51 | MV51 | 60 | 7485 | °C | Furnace | 12 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Mirror image of WE Correlated with 10271 group 12
SHE01:'1#F1:TE_T011'.F_CV | 7945 Open Crown Temperature - Downstream Working End (PV) | Open Crown Temperature - Downstream Working End (PV) | 60 | 7945 | °C | Furnace | 2 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 0 | Mirror image of Refiner Correlated with 10271 group 12
SHE01:'1#F1:TE_T001'.F_CV | 7546 Open Crown Temperature - Port 1 (PV) | Open Crown Temperature - Port 1 (PV) | 60 | 7546 | °C | Furnace | 24 | 26 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes / Sidedness Issue
SHE01:'1#F1:TE_T002'.F_CV | 7746 Open Crown Temperature - Port 2 (PV) | Open Crown Temperature - Port 2 (PV) | 60 | 7746 | °C | Furnace | 24 | 4 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes / Sidedness Issue
SHE01:'1#F1:TE_T003'.F_CV | 7548 Open Crown Temperature - Port 3 (PV) | Open Crown Temperature - Port 3 (PV) | 60 | 7548 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 0 | 0 | 1 | Correlated with 7546 Group 4
SHE01:'1#F1:TE_T004'.F_CV | 7522 Open Crown Temperature - Port 4 (PV) | Open Crown Temperature - Port 4 (PV) | 60 | 7522 | °C | Furnace | 24 | 17 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes Correlated Group 4
SHE01:'1#F1:TE_T005'.F_CV | 7673 Open Crown Temperature - Port 5 (PV) | Open Crown Temperature - Port 5 (PV) | 60 | 7673 | °C | Furnace | 24 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1
SHE01:'1#F1:TE_T006'.F_CV | 7483 Open Crown Temperature - Port 6 (PV) | Open Crown Temperature - Port 6 (PV) | 60 | 7483 | °C | Furnace | 18 | 0 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes / Sidedness Issue
SHE01:'1#F1:TE_T007'.F_CV | 7525 Open Crown Temperature - Port 7 (PV) | Open Crown Temperature - Port 7 (PV) | 60 | 7525 | °C | Furnace | 18 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes / Sidedness Issue Correlated with 10271 group 12
SHE01:'1#F1:TE_T008'.F_CV | 11148 Open Crown Temperature - Port 8 (PV) | Open Crown Temperature - Port 8 (PV) | 60 | 11148 | °C | Furnace | 18 | 0 | 0.1 | 1000 | 1650 |  | 0 | 1 | 0.1 | 1 | 0 | 1 | Correlated with 11148 group 8
SHE01:'1#F3:PID_T012'.F_OP | 31137 Open Crown Temperature - Upstream Refiner (OP) | Open Crown Temperature - Upstream Refiner (OP) | 60 | 31137 | % | Furnace | 12 | 0 | 1 | 1000 | 1650 |  | 0 | 0 | 0.1 | 0 | 1 | 0 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#F3:PID_T012'.F_PV | 10271 C9 (T012) Upstream Refiner | C9 (T012) Upstream Refiner | 60 | 10271 | °C | Furnace | 12 | 21 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 1 | 0 | 1 | Max temp in last 20 minutes / Sidedness Issue
SHE01:'1#F1:TE_T010'.F_CV | 7520 Open Crown Temperature - Upstream Working End (PV) | Open Crown Temperature - Upstream Working End (PV) | 60 | 7520 | °C | Furnace | 4 | 0 | 0.1 | 1000 | 1650 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:TT_T603.F_PV | 7443 Outside Ambient Temperature Measurement | Outside Ambient Temperature Measurement | 60 | 7443 | °C | Furnace | 18 | 0 | 0.1 | -10 | 40 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SCP01:ANEM_001.F_CV | 7999 Outside Windspeed Anemometer | Outside Windspeed Anemometer | 60 | 7999 | m/s | Furnace | 4 | 0 | 1 |  |  |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#FC8:TE_T195'.F_CV | 329 Plant Cooling Water Temp. Meas | Plant Cooling Water Temp. Meas | 60 | 329 | °C | Services | 0 | 0 | 1 | 0 | 60 |  | 0 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:PID_F061'.F_OP | 11105 Port 1 Combustion Air Flow LHS (OP) | Port 1 Combustion Air Flow LHS (OP) | 60 | 11105 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:PID_F061'.F_PV | 11106 Port 1 Combustion Air Flow LHS (PV) | Port 1 Combustion Air Flow LHS (PV) | 60 | 11106 | m³/h | Furnace | 24 | 0 | 10 | 0 | 15000 | 100000 | 0 | 0 | 0.1 | 0 | 0 | 1 | Max flow in last 20 minutes Enable equals to 0 Because it is correlated with 9400
SHE01:'1#FC1:PID_F161'.F_OP | 11108 Port 1 Combustion Air Flow RHS (OP) | Port 1 Combustion Air Flow RHS (OP) | 60 | 11108 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:PID_F161'.F_PV | 11109 Port 1 Combustion Air Flow RHS (PV) | Port 1 Combustion Air Flow RHS (PV) | 60 | 11109 | m³/h | Furnace | 24 | 0 | 10 | 0 | 1500 | 100000 | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC1:PID_F151'.F_PV | 6467 Port 1 Gas Flow (PV) | Port 1 Gas Flow (PV) | 60 | 6467 | m³/h | Furnace | 24 | 0 | 1 | 0 | 1400 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC1:PID_F151'.F_SP | 9402 Port 1 Gas Flow (SP) | Port 1 Gas Flow (SP) | 60 | 9402 | m³/h | Furnace | 24 | 0 | 0 | 0 | 1400 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC2:PID_F062'.F_OP | 11111 Port 2 - 3 Combustion Air Flow LHS (OP) | Port 2 - 3 Combustion Air Flow LHS (OP) | 60 | 11111 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC2:PID_F062'.F_PV | 11112 Port 2 - 3 Combustion Air Flow LHS (PV) | Port 2 - 3 Combustion Air Flow LHS (PV) | 60 | 11112 | m³/h | Furnace | 24 | 0 | 10 | 0 | 28000 | 100001 | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC2:PID_F162'.F_OP | 11114 Port 2 - 3 Combustion Air Flow RHS (OP) | Port 2 - 3 Combustion Air Flow RHS (OP) | 60 | 11114 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC2:PID_F162'.F_PV | 11115 Port 2 - 3 Combustion Air Flow RHS (PV) | Port 2 - 3 Combustion Air Flow RHS (PV) | 60 | 11115 | m³/h | Furnace | 24 | 0 | 10 | 0 | 28000 | 100001 | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC2:PID_F152'.F_PV | 6466 Port 2 Gas Flow (PV) | Port 2 Gas Flow (PV) | 60 | 6466 | m³/h | Furnace | 24 | 0 | 1 | 0 | 1400 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC2:PID_F152'.F_SP | 9400 Port 2 Gas Flow (SP) | Port 2 Gas Flow (SP) | 60 | 9400 | m³/h | Furnace | 24 | 0 | 0 | 0 | 1400 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC2:PID_F153'.F_PV | 6465 Port 3 Gas Flow (PV) | Port 3 Gas Flow (PV) | 60 | 6465 | m³/h | Furnace | 24 | 0 | 1 | 0 | 1400 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC2:PID_F153'.F_SP | 9398 Port 3 Gas Flow (SP) | Port 3 Gas Flow (SP) | 60 | 9398 | m³/h | Furnace | 24 | 0 | 0 | 0 | 1400 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#FC3:PID_F063'.F_OP | 11117 Port 4 - 5 Combustion Air Flow LHS (OP) | Port 4 - 5 Combustion Air Flow LHS (OP) | 60 | 11117 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Not consider from correlated group 2
SHE01:'1#FC3:PID_F063'.F_PV | 11118 Port 4 - 5 Combustion Air Flow LHS (PV) | Port 4 - 5 Combustion Air Flow LHS (PV) | 60 | 11118 | m³/h | Furnace | 24 | 0 | 10 | 0 | 22000 | 100002 | 0 | 0 | 0.1 | 0 | 0 | 1 | Not consider from correlated group 2
SHE01:'1#FC3:PID_F163'.F_OP | 11120 Port 4 - 5 Combustion Air Flow RHS (OP) | Port 4 - 5 Combustion Air Flow RHS (OP) | 60 | 11120 | % | Furnace | 24 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Not consider from correlated group 2
SHE01:'1#FC3:PID_F163'.F_PV | 11121 Port 4 - 5 Combustion Air Flow RHS (PV) | Port 4 - 5 Combustion Air Flow RHS (PV) | 60 | 11121 | m³/h | Furnace | 24 | 0 | 10 | 0 | 22000 | 100002 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#FC3:PID_F154'.F_PV | 6665 Port 4 Gas Flow (PV) | Port 4 Gas Flow (PV) | 60 | 6665 | m³/h | Furnace | 24 | 0 | 1 | 0 | 1400 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#FC3:PID_F154'.F_SP | 9476 Port 4 Gas Flow (SP) | Port 4 Gas Flow (SP) | 60 | 9476 | m³/h | Furnace | 24 | 0 | 0 | 0 | 1400 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC3:PID_F155'.F_PV | 8390 Port 5 Gas Flow (PV) | Port 5 Gas Flow (PV) | 60 | 8390 | m³/h | Furnace | 24 | 0 | 1 | 0 | 600 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#FC3:PID_F155'.F_SP | 9580 Port 5 Gas Flow (SP) | Port 5 Gas Flow (SP) | 60 | 9580 | m³/h | Furnace | 24 | 0 | 0 | 0 | 600 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC4:PID_F064'.F_OP | 11123 Port 6 - 7 Combustion Air Flow LHS (OP) | Port 6 - 7 Combustion Air Flow LHS (OP) | 60 | 11123 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC4:PID_F064'.F_PV | 11124 Port 6 - 7 Combustion Air Flow LHS (PV) | Port 6 - 7 Combustion Air Flow LHS (PV) | 60 | 11124 | m³/h | Furnace | 18 | 0 | 10 | 0 | 16000 | 100003 | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9502 group 14
SHE01:'1#FC4:PID_F164'.F_OP | 11126 Port 6 - 7 Combustion Air Flow RHS (OP)) | Port 6 - 7 Combustion Air Flow RHS (OP)) | 60 | 11126 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC4:PID_F164'.F_PV | 11127 Port 6 - 7 Combustion Air Flow RHS (PV) | Port 6 - 7 Combustion Air Flow RHS (PV) | 60 | 11127 | m³/h | Furnace | 18 | 0 | 10 | 0 | 16000 | 100003 | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9502 group 14
SHE01:'1#FC4:PID_F156'.F_PV | 6585 Port 6 Gas Flow (PV) | Port 6 Gas Flow (PV) | 60 | 6585 | m³/h | Furnace | 18 | 0 | 1 | 0 | 800 |  | 1 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#FC4:PID_F156'.F_SP | 9462 Port 6 Gas Flow (SP) | Port 6 Gas Flow (SP) | 60 | 9462 | m³/h | Furnace | 18 | 0 | 1 | 0 | 600 |  | 0 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC4:PID_F157'.F_PV | 7667 Port 7 Gas Flow (PV) | Port 7 Gas Flow (PV) | 60 | 7667 | m³/h | Furnace | 18 | 0 | 1 | 0 | 800 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9502 group 14
SHE01:'1#FC4:PID_F157'.F_SP | 9502 Port 7 Gas Flow (SP) | Port 7 Gas Flow (SP) | 60 | 9502 | m³/h | Furnace | 18 | 0 | 0 | 0 | 800 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:PID_F065'.F_OP | 11129 Port 8 Combustion Air Flow LHS (OP) | Port 8 Combustion Air Flow LHS (OP) | 60 | 11129 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Correlated with 11137 group 15
SHE01:'1#FC1:PID_F065'.F_PV | 11130 Port 8 Combustion Air Flow LHS (PV) | Port 8 Combustion Air Flow LHS (PV) | 60 | 11130 | m³/h | Furnace | 18 | 0 | 10 | 0 | 6000 | 100004 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#FC1:PID_F165'.F_OP | 11132 Port 8 Combustion Air Flow RHS (OP) | Port 8 Combustion Air Flow RHS (OP) | 60 | 11132 | % | Furnace | 18 | 0 | 1 | 0 | 100 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:PID_F165'.F_PV | 11133 Port 8 Combustion Air Flow RHS (PV) | Port 8 Combustion Air Flow RHS (PV) | 60 | 11133 | m³/h | Furnace | 18 | 0 | 10 | 0 | 6000 | 100004 | 0 | 0 | 0.1 | 0 | 0 | 1 | Ignored from correlated group 16
SHE01:'1#FC1:PID_F158'.F_PV | 11136 Port 8 Gas Flow (PV) | Port 8 Gas Flow (PV) | 60 | 11136 | m³/h | Furnace | 18 | 0 | 1 | 0 | 600 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 11137 group 15
SHE01:'1#FC1:PID_F158'.F_SP | 11137 Port 8 Gas Flow (SP) | Port 8 Gas Flow (SP) | 60 | 11137 | m³/h | Furnace | 18 | 0 | 0 | 0 | 600 |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Ignored from correlated group 16
SHE01:PID_P012.F_PV | 7996 Recirc. Water Pressure Control (PV) | Recirc. Water Pressure Control (PV) | 60 | 7996 | Bar | Furnace | 0 | 0 | 0.1 | 0 | 10 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:'1#F1:TE_T121'.F_CV | 8122 Regenerator Base Temperature Port 1 LHS | Regenerator Base Temperature Port 1 LHS | 60 | 8122 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300021 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T131'.F_CV | 8044 Regenerator Base Temperature Port 1 RHS | Regenerator Base Temperature Port 1 RHS | 60 | 8044 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300021 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T122'.F_CV | 8046 Regenerator Base Temperature Port 2 LHS | Regenerator Base Temperature Port 2 LHS | 60 | 8046 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300022 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T132'.F_CV | 7890 Regenerator Base Temperature Port 2 RHS | Regenerator Base Temperature Port 2 RHS | 60 | 7890 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300022 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T123'.F_CV | 8123 Regenerator Base Temperature Port 3 LHS | Regenerator Base Temperature Port 3 LHS | 60 | 8123 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300023 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T133'.F_CV | 8127 Regenerator Base Temperature Port 3 RHS | Regenerator Base Temperature Port 3 RHS | 60 | 8127 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300023 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T124'.F_CV | 7774 Regenerator Base Temperature Port 4 LHS | Regenerator Base Temperature Port 4 LHS | 60 | 7774 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300024 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T134'.F_CV | 8126 Regenerator Base Temperature Port 4 RHS | Regenerator Base Temperature Port 4 RHS | 60 | 8126 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300024 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T125'.F_CV | 8120 Regenerator Base Temperature Port 5 LHS | Regenerator Base Temperature Port 5 LHS | 60 | 8120 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300025 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T135'.F_CV | 7609 Regenerator Base Temperature Port 5 RHS | Regenerator Base Temperature Port 5 RHS | 60 | 7609 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300025 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T126'.F_CV | 7594 Regenerator Base Temperature Port 6 LHS | Regenerator Base Temperature Port 6 LHS | 60 | 7594 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300026 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T136'.F_CV | 7598 Regenerator Base Temperature Port 6 RHS | Regenerator Base Temperature Port 6 RHS | 60 | 7598 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300026 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T127'.F_CV | 7425 Regenerator Base Temperature Port 7 LHS | Regenerator Base Temperature Port 7 LHS | 60 | 7425 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300027 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T137'.F_CV | 7610 Regenerator Base Temperature Port 7 RHS | Regenerator Base Temperature Port 7 RHS | 60 | 7610 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300027 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T128'.F_CV | 11146 Regenerator Base Temperature Port 8 LHS | Regenerator Base Temperature Port 8 LHS | 60 | 11146 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300028 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T138'.F_CV | 11147 Regenerator Base Temperature Port 8 RHS | Regenerator Base Temperature Port 8 RHS | 60 | 11147 | °C | Furnace | 36 | 0 | 1 | 0 | 1000 | 300028 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T102'.F_CV | 1355 Regenerator Crown Temperature Port 2 LHS | Regenerator Crown Temperature Port 2 LHS | 60 | 1355 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300012 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T112'.F_CV | 1358 Regenerator Crown Temperature Port 2 RHS | Regenerator Crown Temperature Port 2 RHS | 60 | 1358 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300012 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T103'.F_CV | 1356 Regenerator Crown Temperature Port 4 LHS | Regenerator Crown Temperature Port 4 LHS | 60 | 1356 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300014 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T113'.F_CV | 1359 Regenerator Crown Temperature Port 4 RHS | Regenerator Crown Temperature Port 4 RHS | 60 | 1359 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300014 | 0 | 0 | 0.1 | 0 | 0 | 0 | This data is only available for the prediod from 25 Jun 2020 to 03 Jan 2021
SHE01:'1#F1:TE_T104'.F_CV | 15069 Regenerator Crown Temperature Port 6 LHS | Regenerator Crown Temperature Port 6 LHS | 60 | 15069 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300016 | 0 | 0 | 0.1 | 0 | 0 | 1 | Max temp in last 20 minutes
SHE01:'1#F1:TE_T114'.F_CV | 15070 Regenerator Crown Temperature Port 6 RHS | Regenerator Crown Temperature Port 6 RHS | 60 | 15070 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300016 | 0 | 0 | 0.1 | 0 | 0 | 1
SHE01:'1#F1:TE_T105'.F_CV | 11141 Regenerator Crown Temperature Port 8 LHS | Regenerator Crown Temperature Port 8 LHS | 60 | 11141 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300018 | 0 | 0 | 0.1 | 0 | 0 | 1 | Max temp in last 20 minutes
SHE01:'1#F1:TE_T115'.F_CV | 11145 Regenerator Crown Temperature Port 8 RHS | Regenerator Crown Temperature Port 8 RHS | 60 | 11145 | °C | Furnace | 30 | 0 | 1 | 1000 | 1650 | 300018 | 0 | 0 | 0.1 | 0 | 0 | 1 | Max temp in last 20 minutes
SHE01:'1#F2:AN_E023'.F_CV | 11221 Services Building MCC1 - MV67 | Services Building MCC1 - MV67 | 60 | 11221 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 0 | 0.1 | 0 | 0 | 0 | Identify cause(s) of dips in load
SHE01:'1#F2:AN_E019'.F_CV | 11217 Services Building MCC9 Cat 'B' Supply - MV60 | Services Building MCC9 Cat 'B' Supply - MV60 | 60 | 11217 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 0 | 0.1 | 0 | 0 | 0 | What is feed from here?
SHE01:ST_S003.F_PV | 1653 Stirrer Speed Control | Stirrer Speed Control | 60 | 1653 | rpm | Furnace | 4 | 0 | 1 | 0 | 1500 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:TE_T174.F_CV | 11182 Stirrer Water Return Temp.Meas. | Stirrer Water Return Temp.Meas. | 60 | 11182 | °C | Furnace | 0 | 0 | 1 | 0 | 150 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | No signal data for period
SHE01:FT_F193.F_PV | 8344 Total CCCW Flow Measurement | Total CCCW Flow Measurement | 60 | 8344 | l/min | Furnace | 0 | 0 | 100 |  |  |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#FC1:FT_F060'.F_CV | 136 Total Combustion Air Flow Measurement | Total Combustion Air Flow Measurement | 60 | 136 | m³/h | Furnace | 12 | 0 | 10 | 0 | 80000 |  | 1 | 1 | 0.1 | 0 | 1 | 0 | Mean flow in last 20 minutes / Sidedness issue
SHE01:'1#FC3:FT_F160'.F_CV | 135 Total Firm Gas Flow Measurement | Total Firm Gas Flow Measurement | 60 | 135 | m³/h | Furnace | 12 | 0 | 10 | 0 | 5000 |  | 0 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#FC2:F150'.F_CV | 8043 Total Gas Flow | Total Gas Flow | 60 | 8043 | m³/h | Furnace | 12 | 0 | 10 | 0 | 8000 |  | 0 | 0 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:'1#L1:GT_U501'.F_CV | 9282 Tweel Position | Tweel Position | 60 | 9282 | mm | Bath | 2 | 0 | 0.01 |  |  |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:FT_F205.F_CV | 30060 U/S Flowing End Air Flow Measurement | U/S Flowing End Air Flow Measurement | 60 | 30060 | m³/h | Bath | 4 | 0 | 10 | 0 | 4500 |  | 1 | 1 | 0.1 | 0 | 0 | 0
SHE01:'1#F2:AN_E027'.F_CV | 11225 UK5 Feed 1 | UK5 Feed 1 | 60 | 11225 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 1 | 0.1 | 0 | 1 | 0 | Correlated with 11301 group 17
SHE01:'1#F2:AN_E029'.F_CV | 11298 UK5 Feed 2 | UK5 Feed 2 | 60 | 11298 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 1 | 0.1 | 0 | 1 | 0 | Correlated with 11301 group 17
SHE01:'1#F2:AN_E032'.F_CV | 11301 UK5 Total Load (Power) | UK5 Total Load (Power) | 60 | 11301 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 1 | 1 | 0.1 | 0 | 1 | 0
SHE01:'1#F2:AN_E030'.F_CV | 11299 UK6 Feed 1 | UK6 Feed 1 | 60 | 11299 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Is this signal valid?
SHE01:'1#F2:AN_E031'.F_CV | 11300 UK6 Feed 2 | UK6 Feed 2 | 60 | 11300 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Is this signal valid?
SHE01:'1#F2:AN_E033'.F_CV | 11226 UK6 Total Load | UK6 Total Load | 60 | 11226 | kWh | Furnace | 0 | 0 | 1 |  |  |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Is this signal valid?
SHE01:TE_T180.F_PV | 1709 Upstream Flue Damper Temperature | Upstream Flue Damper Temperature | 60 | 1709 | °C | Furnace | 4 | 0 | 1 | 0 | 1350 |  | 0 | 1 | 0.1 | 0 | 0 | 1 | Correlated with 9400 Port 2 Gas Flow (SP)
SHE01:QT_Q003.F_CV | 11384 Wobbe Index (Incoming Gas) | Wobbe Index (Incoming Gas) | 60 | 11384 | Index | Furnace | 12 | 0 | 1 | 1000 | 1500 |  | 1 | 0 | 0.1 | 0 | 0 | 0
SHE01:'1#BC1:PID_F186'.F_PV | 239 Working End Burner Gas Flow RHS (PV) | Working End Burner Gas Flow RHS (PV) | 60 | 239 | m³/h | Furnace | 2 | 0 | 1 | 0 | 200 |  | 0 | 0 | 0.1 | 0 | 0 | 0 | Metering noise
Combined Signals
^Port 1 Combustion Air Flow (PV)
^Port 2 - 3 Combustion Air Flow (PV)
^Port 4 - 5 Combustion Air Flow (PV)
^Port 6 - 7 Combustion Air Flow (PV)
^Port 8 Combustion Air Flow (PV)
^Front Wall Temperature Average (PV)
^Regenerator Crown Temperature Port 2
^Regenerator Crown Temperature Port 4
^Regenerator Crown Temperature Port 6
^Regenerator Crown Temperature Port 8
^Regenerator Base Temperature Port 1
^Regenerator Base Temperature Port 2
^Regenerator Base Temperature Port 3
^Regenerator Base Temperature Port 4
^Regenerator Base Temperature Port 5
^Regenerator Base Temperature Port 6
^Regenerator Base Temperature Port 7
^Regenerator Base Temperature Port 8